## Modbusvariablen
Modbus Interface Variables |  |  |  | Version: 20220112
Mod. Add. | Read/Write | Factor | VariableName | Description | MinRealValue | MaxRealValue
heatCircuits
heatCircuit[0]
0 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[0].tempRoom.state.msgId | Message ID of the room temperature sensor.
1 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[0].tempRoom.values.actValue | Actual room temperature [1/10°C].
2 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[0].values.selectedSetTemp | Current set room temperature [1/10°C]. Means set temperature plus offset.
3 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[0].values.setValue | Room set temperature [1/10°C].
4 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[0].param.normalSetTemp | Room set temperature for heating circuit [1/10°C] | 10 | 30
5 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[0].param.reducedSetTemp | Room set temperature for reduced operating mode [1/10°C] | 10 | 30
6 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[0].param.offsetRoomTemp | Manual offset to the setTempNormal / setTempReduced [1/10°C] | -25 | 25
7 | R/W | 1 | APPL.CtrlAppl.sParam.heatCircuit[0].param.operatingMode | Heating circuit operating mode. Selection from "0...Standby" / "1...Timer" / "2...Day" / "3...Night" / "4...Vacation" / "5...Party" / "8...Extern" | 0 | 8
8 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[0].values.heatRequest | Heatcircuit's heat request
9 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[0].humidityRoom.state.msgId | Message ID of the humidity sensor.
10 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[0].humidityRoom.values.actValue | Actual room humidity [%]
11 | R/W | 1 | APPL.CtrlAppl.sParam.heatCircuit[0].param.external.coolRequest | Cool request set by external controller | 0 | 1
12 | R/W | 1 | APPL.CtrlAppl.sParam.heatCircuit[0].param.external.heatRequest | Heat request set by external controller | 0 | 1
13 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[0].param.external.inflowSetTemp | Flow set temperature from external controller [1/10°C] | 0 | 70
14 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[0].param.excessEnergyTemp.value | Excess energy target temp [1/10°C] | 10 | 30
15 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[0].heatCircuitMixer.flowTemp.values.actValue | Actual heat circuit flow temperature [1/10°C].
16 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[0].tempReflux.values.actValue | Actual heat circuit reflux temperature [1/10°C].
17 | R | 100 | APPL.CtrlAppl.sParam.heatCircuit[0].heatCircuitMixer.mixer.values.setValueScaled | Actual heat circuit mixer position [+/-100%].
18 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[0].pump.values.setValueB | Actual value of the heat circuit pump.
19 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[0].values.heatRequest | Heat Request
20 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[0].values.coolRequest | Cool request
21 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[0].values.useExcessEnergy | Use Excess Energy
22 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[0].param.excessEnergyTempCool.value | Excess energy target cool temp [1/10°C] | 10 | 30
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
heatCircuit[1]
50 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[1].tempRoom.state.msgId | Message ID of the room temperature sensor.
51 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[1].tempRoom.values.actValue | Actual room temperature [1/10°C].
52 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[1].values.selectedSetTemp | Current set room temperature [1/10°C]. Means set temperature plus offset.
53 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[1].values.setValue | Room set temperature [1/10°C].
54 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[1].param.normalSetTemp | Room set temperature for heating circuit [1/10°C] | 10 | 30
55 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[1].param.reducedSetTemp | Room set temperature for reduced operating mode [1/10°C] | 10 | 30
56 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[1].param.offsetRoomTemp | Manual offset to the setTempNormal / setTempReduced [1/10°C] | -25 | 25
57 | R/W | 1 | APPL.CtrlAppl.sParam.heatCircuit[1].param.operatingMode | Heating circuit operating mode. Selection from "0...Standby" / "1...Timer" / "2...Day" / "3...Night" / "4...Vacation" / "5...Party" / "8...Extern" | 0 | 8
58 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[1].values.heatRequest | Heatcircuit's heat request
59 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[1].humidityRoom.state.msgId | Message ID of the humidity sensor.
60 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[1].humidityRoom.values.actValue | Actual room humidity [%]
61 | R/W | 1 | APPL.CtrlAppl.sParam.heatCircuit[1].param.external.coolRequest | Cool request set by external controller | 0 | 1
62 | R/W | 1 | APPL.CtrlAppl.sParam.heatCircuit[1].param.external.heatRequest | Heat request set by external controller | 0 | 1
63 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[1].param.external.inflowSetTemp | Flow set temperature from external controller [1/10°C] | 0 | 70
64 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[1].param.excessEnergyTemp.value | Excess energy target temp [1/10°C] | 10 | 30
65 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[1].heatCircuitMixer.flowTemp.values.actValue | Actual heat circuit flow temperature [1/10°C].
66 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[1].tempReflux.values.actValue | Actual heat circuit reflux temperature [1/10°C].
67 | R | 100 | APPL.CtrlAppl.sParam.heatCircuit[1].heatCircuitMixer.mixer.values.setValueScaled | Actual heat circuit mixer position [+/-100%].
68 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[1].pump.values.setValueB | Actual value of the heat circuit pump.
69 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[1].values.heatRequest | Heat Request
70 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[1].values.coolRequest | Cool request
71 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[1].values.useExcessEnergy | Use Excess Energy
72 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[1].param.excessEnergyTempCool.value | Excess energy target cool temp [1/10°C] | 10 | 30
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
heatCircuit[2]
100 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[2].tempRoom.state.msgId | Message ID of the room temperature sensor.
101 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[2].tempRoom.values.actValue | Actual room temperature [1/10°C].
102 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[2].values.selectedSetTemp | Current set room temperature [1/10°C]. Means set temperature plus offset.
103 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[2].values.setValue | Room set temperature [1/10°C].
104 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[2].param.normalSetTemp | Room set temperature for heating circuit [1/10°C] | 10 | 30
105 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[2].param.reducedSetTemp | Room set temperature for reduced operating mode [1/10°C] | 10 | 30
106 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[2].param.offsetRoomTemp | Manual offset to the setTempNormal / setTempReduced [1/10°C] | -25 | 25
107 | R/W | 1 | APPL.CtrlAppl.sParam.heatCircuit[2].param.operatingMode | Heating circuit operating mode. Selection from "0...Standby" / "1...Timer" / "2...Day" / "3...Night" / "4...Vacation" / "5...Party" / "8...Extern" | 0 | 8
108 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[2].values.heatRequest | Heatcircuit's heat request
109 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[2].humidityRoom.state.msgId | Message ID of the humidity sensor.
110 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[2].humidityRoom.values.actValue | Actual room humidity [%]
111 | R/W | 1 | APPL.CtrlAppl.sParam.heatCircuit[2].param.external.coolRequest | Cool request set by external controller | 0 | 1
112 | R/W | 1 | APPL.CtrlAppl.sParam.heatCircuit[2].param.external.heatRequest | Heat request set by external controller | 0 | 1
113 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[2].param.external.inflowSetTemp | Flow set temperature from external controller [1/10°C] | 0 | 70
114 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[2].param.excessEnergyTemp.value | Excess energy target temp [1/10°C] | 10 | 30
115 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[2].heatCircuitMixer.flowTemp.values.actValue | Actual heat circuit flow temperature [1/10°C].
116 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[2].tempReflux.values.actValue | Actual heat circuit reflux temperature [1/10°C].
117 | R | 100 | APPL.CtrlAppl.sParam.heatCircuit[2].heatCircuitMixer.mixer.values.setValueScaled | Actual heat circuit mixer position [+/-100%].
118 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[2].pump.values.setValueB | Actual value of the heat circuit pump.
119 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[2].values.heatRequest | Heat Request
120 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[2].values.coolRequest | Cool request
121 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[2].values.useExcessEnergy | Use Excess Energy
122 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[2].param.excessEnergyTempCool.value | Excess energy target cool temp [1/10°C] | 10 | 30
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
heatCircuit[3]
150 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[3].tempRoom.state.msgId | Message ID of the room temperature sensor.
151 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[3].tempRoom.values.actValue | Actual room temperature [1/10°C].
152 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[3].values.selectedSetTemp | Current set room temperature [1/10°C]. Means set temperature plus offset.
153 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[3].values.setValue | Room set temperature [1/10°C].
154 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[3].param.normalSetTemp | Room set temperature for heating circuit [1/10°C] | 10 | 30
155 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[3].param.reducedSetTemp | Room set temperature for reduced operating mode [1/10°C] | 10 | 30
156 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[3].param.offsetRoomTemp | Manual offset to the setTempNormal / setTempReduced [1/10°C] | -25 | 25
157 | R/W | 1 | APPL.CtrlAppl.sParam.heatCircuit[3].param.operatingMode | Heating circuit operating mode. Selection from "0...Standby" / "1...Timer" / "2...Day" / "3...Night" / "4...Vacation" / "5...Party" / "8...Extern" | 0 | 8
158 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[3].values.heatRequest | Heatcircuit's heat request
159 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[3].humidityRoom.state.msgId | Message ID of the humidity sensor.
160 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[3].humidityRoom.values.actValue | Actual room humidity [%]
161 | R/W | 1 | APPL.CtrlAppl.sParam.heatCircuit[3].param.external.coolRequest | Cool request set by external controller | 0 | 1
162 | R/W | 1 | APPL.CtrlAppl.sParam.heatCircuit[3].param.external.heatRequest | Heat request set by external controller | 0 | 1
163 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[3].param.external.inflowSetTemp | Flow set temperature from external controller [1/10°C] | 0 | 70
164 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[3].param.excessEnergyTemp.value | Excess energy target temp [1/10°C] | 10 | 30
165 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[3].heatCircuitMixer.flowTemp.values.actValue | Actual heat circuit flow temperature [1/10°C].
166 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[3].tempReflux.values.actValue | Actual heat circuit reflux temperature [1/10°C].
167 | R | 100 | APPL.CtrlAppl.sParam.heatCircuit[3].heatCircuitMixer.mixer.values.setValueScaled | Actual heat circuit mixer position [+/-100%].
168 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[3].pump.values.setValueB | Actual value of the heat circuit pump.
169 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[3].values.heatRequest | Heat Request
170 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[3].values.coolRequest | Cool request
171 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[3].values.useExcessEnergy | Use Excess Energy
172 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[3].param.excessEnergyTempCool.value | Excess energy target cool temp [1/10°C] | 10 | 30
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
heatCircuit[4]
200 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[4].tempRoom.state.msgId | Message ID of the room temperature sensor.
201 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[4].tempRoom.values.actValue | Actual room temperature [1/10°C].
202 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[4].values.selectedSetTemp | Current set room temperature [1/10°C]. Means set temperature plus offset.
203 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[4].values.setValue | Room set temperature [1/10°C].
204 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[4].param.normalSetTemp | Room set temperature for heating circuit [1/10°C] | 10 | 30
205 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[4].param.reducedSetTemp | Room set temperature for reduced operating mode [1/10°C] | 10 | 30
206 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[4].param.offsetRoomTemp | Manual offset to the setTempNormal / setTempReduced [1/10°C] | -25 | 25
207 | R/W | 1 | APPL.CtrlAppl.sParam.heatCircuit[4].param.operatingMode | Heating circuit operating mode. Selection from "0...Standby" / "1...Timer" / "2...Day" / "3...Night" / "4...Vacation" / "5...Party" / "8...Extern" | 0 | 8
208 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[4].values.heatRequest | Heatcircuit's heat request
209 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[4].humidityRoom.state.msgId | Message ID of the humidity sensor.
210 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[4].humidityRoom.values.actValue | Actual room humidity [%]
211 | R/W | 1 | APPL.CtrlAppl.sParam.heatCircuit[4].param.external.coolRequest | Cool request set by external controller | 0 | 1
212 | R/W | 1 | APPL.CtrlAppl.sParam.heatCircuit[4].param.external.heatRequest | Heat request set by external controller | 0 | 1
213 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[4].param.external.inflowSetTemp | Flow set temperature from external controller [1/10°C] | 0 | 70
214 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[4].param.excessEnergyTemp.value | Excess energy target temp [1/10°C] | 10 | 30
215 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[4].heatCircuitMixer.flowTemp.values.actValue | Actual heat circuit flow temperature [1/10°C].
216 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[4].tempReflux.values.actValue | Actual heat circuit reflux temperature [1/10°C].
217 | R | 100 | APPL.CtrlAppl.sParam.heatCircuit[4].heatCircuitMixer.mixer.values.setValueScaled | Actual heat circuit mixer position [+/-100%].
218 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[4].pump.values.setValueB | Actual value of the heat circuit pump.
219 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[4].values.heatRequest | Heat Request
220 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[4].values.coolRequest | Cool request
221 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[4].values.useExcessEnergy | Use Excess Energy
222 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[4].param.excessEnergyTempCool.value | Excess energy target cool temp [1/10°C] | 10 | 30
223
224
225
226
227
228
229
230
231
232
233
234
235
236
237
238
239
240
241
242
243
244
245
246
247
248
249
heatCircuit[5]
250 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[5].tempRoom.state.msgId | Message ID of the room temperature sensor.
251 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[5].tempRoom.values.actValue | Actual room temperature [1/10°C].
252 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[5].values.selectedSetTemp | Current set room temperature [1/10°C]. Means set temperature plus offset.
253 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[5].values.setValue | Room set temperature [1/10°C].
254 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[5].param.normalSetTemp | Room set temperature for heating circuit [1/10°C] | 10 | 30
255 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[5].param.reducedSetTemp | Room set temperature for reduced operating mode [1/10°C] | 10 | 30
256 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[5].param.offsetRoomTemp | Manual offset to the setTempNormal / setTempReduced [1/10°C] | -25 | 25
257 | R/W | 1 | APPL.CtrlAppl.sParam.heatCircuit[5].param.operatingMode | Heating circuit operating mode. Selection from "0...Standby" / "1...Timer" / "2...Day" / "3...Night" / "4...Vacation" / "5...Party" / "8...Extern" | 0 | 8
258 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[5].values.heatRequest | Heatcircuit's heat request
259 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[5].humidityRoom.state.msgId | Message ID of the humidity sensor.
260 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[5].humidityRoom.values.actValue | Actual room humidity [%]
261 | R/W | 1 | APPL.CtrlAppl.sParam.heatCircuit[5].param.external.coolRequest | Cool request set by external controller | 0 | 1
262 | R/W | 1 | APPL.CtrlAppl.sParam.heatCircuit[5].param.external.heatRequest | Heat request set by external controller | 0 | 1
263 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[5].param.external.inflowSetTemp | Flow set temperature from external controller [1/10°C] | 0 | 70
264 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[5].param.excessEnergyTemp.value | Excess energy target temp [1/10°C] | 10 | 30
265 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[5].heatCircuitMixer.flowTemp.values.actValue | Actual heat circuit flow temperature [1/10°C].
266 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[5].tempReflux.values.actValue | Actual heat circuit reflux temperature [1/10°C].
267 | R | 100 | APPL.CtrlAppl.sParam.heatCircuit[5].heatCircuitMixer.mixer.values.setValueScaled | Actual heat circuit mixer position [+/-100%].
268 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[5].pump.values.setValueB | Actual value of the heat circuit pump.
269 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[5].values.heatRequest | Heat Request
270 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[5].values.coolRequest | Cool request
271 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[5].values.useExcessEnergy | Use Excess Energy
272 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[5].param.excessEnergyTempCool.value | Excess energy target cool temp [1/10°C] | 10 | 30
273
274
275
276
277
278
279
280
281
282
283
284
285
286
287
288
289
290
291
292
293
294
295
296
297
298
299
heatCircuit[6]
300 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[6].tempRoom.state.msgId | Message ID of the room temperature sensor.
301 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[6].tempRoom.values.actValue | Actual room temperature [1/10°C].
302 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[6].values.selectedSetTemp | Current set room temperature [1/10°C]. Means set temperature plus offset.
303 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[6].values.setValue | Room set temperature [1/10°C].
304 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[6].param.normalSetTemp | Room set temperature for heating circuit [1/10°C] | 10 | 30
305 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[6].param.reducedSetTemp | Room set temperature for reduced operating mode [1/10°C] | 10 | 30
306 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[6].param.offsetRoomTemp | Manual offset to the setTempNormal / setTempReduced [1/10°C] | -25 | 25
307 | R/W | 1 | APPL.CtrlAppl.sParam.heatCircuit[6].param.operatingMode | Heating circuit operating mode. Selection from "0...Standby" / "1...Timer" / "2...Day" / "3...Night" / "4...Vacation" / "5...Party" / "8...Extern" | 0 | 8
308 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[6].values.heatRequest | Heatcircuit's heat request
309 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[6].humidityRoom.state.msgId | Message ID of the humidity sensor.
310 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[6].humidityRoom.values.actValue | Actual room humidity [%]
311 | R/W | 1 | APPL.CtrlAppl.sParam.heatCircuit[6].param.external.coolRequest | Cool request set by external controller | 0 | 1
312 | R/W | 1 | APPL.CtrlAppl.sParam.heatCircuit[6].param.external.heatRequest | Heat request set by external controller | 0 | 1
313 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[6].param.external.inflowSetTemp | Flow set temperature from external controller [1/10°C] | 0 | 70
314 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[6].param.excessEnergyTemp.value | Excess energy target temp [1/10°C] | 10 | 30
315 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[6].heatCircuitMixer.flowTemp.values.actValue | Actual heat circuit flow temperature [1/10°C].
316 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[6].tempReflux.values.actValue | Actual heat circuit reflux temperature [1/10°C].
317 | R | 100 | APPL.CtrlAppl.sParam.heatCircuit[6].heatCircuitMixer.mixer.values.setValueScaled | Actual heat circuit mixer position [+/-100%].
318 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[6].pump.values.setValueB | Actual value of the heat circuit pump.
319 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[6].values.heatRequest | Heat Request
320 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[6].values.coolRequest | Cool request
321 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[6].values.useExcessEnergy | Use Excess Energy
322 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[6].param.excessEnergyTempCool.value | Excess energy target cool temp [1/10°C] | 10 | 30
323
324
325
326
327
328
329
330
331
332
333
334
335
336
337
338
339
340
341
342
343
344
345
346
347
348
349
heatCircuit[7]
350 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[7].tempRoom.state.msgId | Message ID of the room temperature sensor.
351 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[7].tempRoom.values.actValue | Actual room temperature [1/10°C].
352 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[7].values.selectedSetTemp | Current set room temperature [1/10°C]. Means set temperature plus offset.
353 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[7].values.setValue | Room set temperature [1/10°C].
354 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[7].param.normalSetTemp | Room set temperature for heating circuit [1/10°C] | 10 | 30
355 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[7].param.reducedSetTemp | Room set temperature for reduced operating mode [1/10°C] | 10 | 30
356 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[7].param.offsetRoomTemp | Manual offset to the setTempNormal / setTempReduced [1/10°C] | -25 | 25
357 | R/W | 1 | APPL.CtrlAppl.sParam.heatCircuit[7].param.operatingMode | Heating circuit operating mode. Selection from "0...Standby" / "1...Timer" / "2...Day" / "3...Night" / "4...Vacation" / "5...Party" / "8...Extern" | 0 | 8
358 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[7].values.heatRequest | Heatcircuit's heat request
359 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[7].humidityRoom.state.msgId | Message ID of the humidity sensor.
360 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[7].humidityRoom.values.actValue | Actual room humidity [%]
361 | R/W | 1 | APPL.CtrlAppl.sParam.heatCircuit[7].param.external.coolRequest | Cool request set by external controller | 0 | 1
362 | R/W | 1 | APPL.CtrlAppl.sParam.heatCircuit[7].param.external.heatRequest | Heat request set by external controller | 0 | 1
363 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[7].param.external.inflowSetTemp | Flow set temperature from external controller [1/10°C] | 0 | 70
364 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[7].param.excessEnergyTemp.value | Excess energy target temp [1/10°C] | 10 | 30
365 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[7].heatCircuitMixer.flowTemp.values.actValue | Actual heat circuit flow temperature [1/10°C].
366 | R | 10 | APPL.CtrlAppl.sParam.heatCircuit[7].tempReflux.values.actValue | Actual heat circuit reflux temperature [1/10°C].
367 | R | 100 | APPL.CtrlAppl.sParam.heatCircuit[7].heatCircuitMixer.mixer.values.setValueScaled | Actual heat circuit mixer position [+/-100%].
368 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[7].pump.values.setValueB | Actual value of the heat circuit pump.
369 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[7].values.heatRequest | Heat Request
370 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[7].values.coolRequest | Cool request
371 | R | 1 | APPL.CtrlAppl.sParam.heatCircuit[7].values.useExcessEnergy | Use Excess Energy
372 | R/W | 10 | APPL.CtrlAppl.sParam.heatCircuit[7].param.excessEnergyTempCool.value | Excess energy target cool temp [1/10°C] | 10 | 30
373
374
375
376
377
378
379
380
381
382
383
384
385
386
387
388
389
390
391
392
393
394
395
396
397
398
399
hotWaterTanks
hotWaterTank[0]
400 | R | 1 | APPL.CtrlAppl.sParam.hotWaterTank[0].topTemp.state.msgId | Message ID of the top temperature sensor. (0...no error)
401 | R | 10 | APPL.CtrlAppl.sParam.hotWaterTank[0].topTemp.values.actValue | Hot water tank top temperature [1/10°C].
402 | R/W | 10 | APPL.CtrlAppl.sParam.hotWaterTank[0].param.normalSetTempMax.value | Hot water tank set temperature [1/10°C]. | 0 | 52
403 | R/W | 1 | APPL.CtrlAppl.sParam.hotWaterTank[0].param.operatingMode | Operating mode hot-water tank. Select from: 0...Off, 1...Time program, 2...Operation without temperature reduction, 3...Forced HW tank load (temporary operating mode) | 0 | 3
404 | R/W | 10 | APPL.CtrlAppl.sParam.hotWaterTank[0].param.excessEnergyTemp.value | Excess energy target temp | 0 | 70
405 | R | 1 | APPL.CtrlAppl.sParam.hotWaterTank[0].values.heatRequestTop | Heat Request
406 | R | 1 | APPL.CtrlAppl.sParam.hotWaterTank[0].values.useExcessEnergy | Use Excess Energy
407 | R/W | 1 | APPL.CtrlAppl.sParam.hotWaterTank[0].param.reducedSetTempMax.value | reduced Set temperature | 0 | 52
408
409
410
411
412
413
414
415
416
417
418
419
420
421
422
423
424
425
426
427
428
429
430
431
432
433
434
435
436
437
438
439
440
441
442
443
444
445
446
447
448
449
hotWaterTank[1]
450 | R | 1 | APPL.CtrlAppl.sParam.hotWaterTank[1].topTemp.state.msgId | Message ID of the top temperature sensor. (0...no error)
451 | R | 10 | APPL.CtrlAppl.sParam.hotWaterTank[1].topTemp.values.actValue | Hot water tank top temperature [1/10°C].
452 | R/W | 10 | APPL.CtrlAppl.sParam.hotWaterTank[1].param.normalSetTempMax.value | Hot water tank set temperature [1/10°C]. | 0 | 52
453 | R/W | 1 | APPL.CtrlAppl.sParam.hotWaterTank[1].param.operatingMode | Operating mode hot-water tank. Select from: 0...Off, 1...Time program, 2...Operation without temperature reduction, 3...Forced HW tank load (temporary operating mode) | 0 | 3
454 | R/W | 10 | APPL.CtrlAppl.sParam.hotWaterTank[1].param.excessEnergyTemp.value | Excess energy target temp | 0 | 70
455 | R | 1 | APPL.CtrlAppl.sParam.hotWaterTank[1].values.heatRequestTop | Heat Request
456 | R | 1 | APPL.CtrlAppl.sParam.hotWaterTank[1].values.useExcessEnergy | Use Excess Energy
457 | R/W | 1 | APPL.CtrlAppl.sParam.hotWaterTank[1].param.reducedSetTempMax.value | reduced Set temperature | 0 | 52
458
459
460
461
462
463
464
465
466
467
468
469
470
471
472
473
474
475
476
477
478
479
480
481
482
483
484
485
486
487
488
489
490
491
492
493
494
495
496
497
498
499
hotWaterTank[2]
500 | R | 1 | APPL.CtrlAppl.sParam.hotWaterTank[2].topTemp.state.msgId | Message ID of the top temperature sensor. (0...no error)
501 | R | 10 | APPL.CtrlAppl.sParam.hotWaterTank[2].topTemp.values.actValue | Hot water tank top temperature [1/10°C].
502 | R/W | 10 | APPL.CtrlAppl.sParam.hotWaterTank[2].param.normalSetTempMax.value | Hot water tank set temperature [1/10°C]. | 0 | 52
503 | R/W | 1 | APPL.CtrlAppl.sParam.hotWaterTank[2].param.operatingMode | Operating mode hot-water tank. Select from: 0...Off, 1...Time program, 2...Operation without temperature reduction, 3...Forced HW tank load (temporary operating mode) | 0 | 3
504 | R/W | 10 | APPL.CtrlAppl.sParam.hotWaterTank[2].param.excessEnergyTemp.value | Excess energy target temp | 0 | 70
505 | R | 1 | APPL.CtrlAppl.sParam.hotWaterTank[2].values.heatRequestTop | Heat Request
506 | R | 1 | APPL.CtrlAppl.sParam.hotWaterTank[2].values.useExcessEnergy | Use Excess Energy
507 | R/W | 1 | APPL.CtrlAppl.sParam.hotWaterTank[2].param.reducedSetTempMax.value | reduced Set temperature | 0 | 52
508
509
510
511
512
513
514
515
516
517
518
519
520
521
522
523
524
525
526
527
528
529
530
531
532
533
534
535
536
537
538
539
540
541
542
543
544
545
546
547
548
549
hotWaterTank[3]
550 | R | 1 | APPL.CtrlAppl.sParam.hotWaterTank[3].topTemp.state.msgId | Message ID of the top temperature sensor. (0...no error)
551 | R | 10 | APPL.CtrlAppl.sParam.hotWaterTank[3].topTemp.values.actValue | Hot water tank top temperature [1/10°C].
552 | R/W | 10 | APPL.CtrlAppl.sParam.hotWaterTank[3].param.normalSetTempMax.value | Hot water tank set temperature [1/10°C]. | 0 | 52
553 | R/W | 1 | APPL.CtrlAppl.sParam.hotWaterTank[3].param.operatingMode | Operating mode hot-water tank. Select from: 0...Off, 1...Time program, 2...Operation without temperature reduction, 3...Forced HW tank load (temporary operating mode) | 0 | 3
554 | R/W | 10 | APPL.CtrlAppl.sParam.hotWaterTank[3].param.excessEnergyTemp.value | Excess energy target temp | 0 | 70
555 | R | 1 | APPL.CtrlAppl.sParam.hotWaterTank[3].values.heatRequestTop | Heat Request
556 | R | 1 | APPL.CtrlAppl.sParam.hotWaterTank[3].values.useExcessEnergy | Use Excess Energy
557 | R/W | 1 | APPL.CtrlAppl.sParam.hotWaterTank[3].param.reducedSetTempMax.value | reduced Set temperature | 0 | 52
558
559
560
561
562
563
564
565
566
567
568
569
570
571
572
573
574
575
576
577
578
579
580
581
582
583
584
585
586
587
588
589
590
591
592
593
594
595
596
597
598
599
bufferTanks
bufferTank[0]
600 | R | 1 | APPL.CtrlAppl.sParam.bufferTank[0].topTemp.state.msgId | Message ID of the top temperature sensor.
601 | R | 10 | APPL.CtrlAppl.sParam.bufferTank[0].topTemp.values.actValue | Actual top temperature [1/10°C].
602 | R | 1 | APPL.CtrlAppl.sParam.bufferTank[0].midTemp.state.msgId | Message ID of the middle temperature sensor.
603 | R | 10 | APPL.CtrlAppl.sParam.bufferTank[0].midTemp.values.actValue | Actual middle temperature [1/10°C].
604 | R/W | 10 | APPL.CtrlAppl.sParam.bufferTank[0].param.backupTemp | Minimum buffer temperature [1/10°C]. Below this temperature the buffer sets a heat request. Used to maintain a minimum energy level in the buffer to speed up heating if heat is requested. | 0 | 90
605 | R/W | 10 | APPL.CtrlAppl.sParam.bufferTank[0].param.minSetTemp | Minimum set temperature [1/10°C]. The buffer is loaded at least with this temperature. | 20 | 90
606 | R/W | 10 | APPL.CtrlAppl.sParam.bufferTank[0].param.coolSetTemp | Cooling set temperature [1/10°C]. The buffer is cooled at least with this temperature. | 0 | 99
607 | R | 1 | APPL.CtrlAppl.sParam.bufferTank[0].values.heatRequestTop | Heat Request
608 | R | 1 | APPL.CtrlAppl.sParam.bufferTank[0].values.coolRequestBot | Cool request
609 | R | 1 | APPL.CtrlAppl.sParam.bufferTank[0].values.useExcessEnergy | Use Excess Energy
610 | R/W | 10 | APPL.CtrlAppl.sParam.bufferTank[0].param.excessEnergyTemp.value | Excess energy target heat temp | 0 | 95
611 | R/W | 10 | APPL.CtrlAppl.sParam.bufferTank[0].param.excessEnergyTempCool.value | Excess energy target cool temp | 0 | 70
612
613
614
615
616
617
618
619
620
621
622
623
624
bufferTank[1]
625 | R | 1 | APPL.CtrlAppl.sParam.bufferTank[1].topTemp.state.msgId | Message ID of the top temperature sensor.
626 | R | 10 | APPL.CtrlAppl.sParam.bufferTank[1].topTemp.values.actValue | Actual top temperature [1/10°C].
627 | R | 1 | APPL.CtrlAppl.sParam.bufferTank[1].midTemp.state.msgId | Message ID of the middle temperature sensor.
628 | R | 10 | APPL.CtrlAppl.sParam.bufferTank[1].midTemp.values.actValue | Actual middle temperature [1/10°C].
629 | R/W | 10 | APPL.CtrlAppl.sParam.bufferTank[1].param.backupTemp | Minimum buffer temperature [1/10°C]. Below this temperature the buffer sets a heat request. Used to maintain a minimum energy level in the buffer to speed up heating if heat is requested. | 0 | 90
630 | R/W | 10 | APPL.CtrlAppl.sParam.bufferTank[1].param.minSetTemp | Minimum set temperature [1/10°C]. The buffer is loaded at least with this temperature. | 20 | 90
631 | R/W | 10 | APPL.CtrlAppl.sParam.bufferTank[1].param.coolSetTemp | Cooling set temperature [1/10°C]. The buffer is cooled at least with this temperature. | 0 | 99
632 | R | 1 | APPL.CtrlAppl.sParam.bufferTank[1].values.heatRequestTop | Heat Request
633 | R | 1 | APPL.CtrlAppl.sParam.bufferTank[1].values.coolRequestBot | Cool request
634 | R | 1 | APPL.CtrlAppl.sParam.bufferTank[1].values.useExcessEnergy | Use Excess Energy
635 | R/W | 10 | APPL.CtrlAppl.sParam.bufferTank[1].param.excessEnergyTemp.value | Excess energy target heat temp | 0 | 95
636 | R/W | 10 | APPL.CtrlAppl.sParam.bufferTank[1].param.excessEnergyTempCool.value | Excess energy target cool temp | 0 | 70
637
638
639
640
641
642
643
644
645
646
647
648
649
bufferTank[2]
650
651
652
653
654
655
656
657
658
659
660
661
662
663
664
665
666
667
668
669
670
671
672
673
674
bufferTank[3]
675
676
677
678
679
680
681
682
683
684
685
686
687
688
689
690
691
692
693
694
695
696
697
698
699
heatpumps
heatpump[0]
700 | R | 0.00027778 | APPL.CtrlAppl.sStatisticalData.heatpump[0].consumption.operatingtime | Operating hours [h].
701 | R | 1 | APPL.CtrlAppl.sStatisticalData.heatpump[0].consumption.energy | Total accumulated heating energy [kWh]
702 | R | 1 | APPL.CtrlAppl.sStatisticalData.heatpump[0].consumption.electricalenergy | Total accumulated electrical energy [kWh]
703 | R | 1 | APPL.CtrlAppl.sParam.heatpump[0].values.heatpumpState | State heatpump. 0...Stanby, 1...PreRun, 2...AutomaticHeat, 3...Defrost, 4...AutomaticCool, 5...PostRun, 7...SafetyShutdown, 8...Error
704 | R | 1 | APPL.CtrlAppl.sParam.heatpump[0].TempHeatFlow.state.msgId | Message ID of the flow temperature sensor.
705 | R | 10 | APPL.CtrlAppl.sParam.heatpump[0].TempHeatFlow.values.actValue | Actual flow temperature [1/10°C].
706 | R | 1 | APPL.CtrlAppl.sParam.heatpump[0].HeatMeter.values.power | Actual power consumtion [kW]
707 | R | 1 | APPL.CtrlAppl.sParam.heatpump[0].ElectricEnergyMeter.values.power | Actual power consumtion [W]
708 | R | 10 | APPL.CtrlAppl.sParam.heatpump[0].TempSourceIn.values.actValue | Actual Source In temperature [1/10°C]
709 | R | 10 | APPL.CtrlAppl.sParam.heatpump[0].TempSourceOut.values.actValue | Actual Source Out temperature [1/10°C]
710 | R | 10 | APPL.CtrlAppl.sParam.heatpump[0].TempHeatReflux.values.actValue | Actual reflux temperature [1/10°C]
711 | R | 100 | APPL.CtrlAppl.sParam.heatpump[0].Source.values.setValueScaled | Source side actuator [1/10°C]
712 | R | 100 | APPL.CtrlAppl.sParam.heatpump[0].CircPump.values.setValueScaled | Heat side actuator
713 | R/W | 1 | APPL.CtrlAppl.sParam.heatpump[0].param.operatingMode | Heat pump operating mode. Selection from "0…Aus" / "1…Ein" / "2…Backup" | 0 | 2
714 | R | 1 | APPL.CtrlAppl.sDiagnosisData.heatpump[0].excessEnergy
715 | R | 0.001 | APPL.CtrlAppl.sStatisticalData.heatpump[0].consumption.energy | Total accumulated heating energy [MWh]
716 | R | 0.001 | APPL.CtrlAppl.sStatisticalData.heatpump[0].consumption.electricalenergy | Total accumulated electrical energy [MWh]
717 | R | 1 | APPL.CtrlAppl.sParam.heatpump[0].values.consumingExcessEnergy | Consuming Excess Energy
718 | R | 100 | APPL.CtrlAppl.sParam.heatpump[0].Compressor.analogOut.values.setValueScaled | Set value compressor
719 | R | 10 | APPL.CtrlAppl.sParam.heatpump[0].values.setTemp | Set temperature heat pump
720
721
722
723
724
heatpump[1]
725 | R | 0.00027778 | APPL.CtrlAppl.sStatisticalData.heatpump[1].consumption.operatingtime | Operating hours [h].
726 | R | 1 | APPL.CtrlAppl.sStatisticalData.heatpump[1].consumption.energy | Total accumulated heating energy [kWh]
727 | R | 1 | APPL.CtrlAppl.sStatisticalData.heatpump[1].consumption.electricalenergy | Total accumulated electrical energy [kWh]
728 | R | 1 | APPL.CtrlAppl.sParam.heatpump[1].values.heatpumpState | State heatpump. 0...Stanby, 1...PreRun, 2...AutomaticHeat, 3...Defrost, 4...AutomaticCool, 5...PostRun, 7...SafetyShutdown, 8...Error
729 | R | 1 | APPL.CtrlAppl.sParam.heatpump[1].TempHeatFlow.state.msgId | Message ID of the flow temperature sensor.
730 | R | 10 | APPL.CtrlAppl.sParam.heatpump[1].TempHeatFlow.values.actValue | Actual flow temperature [1/10°C].
731 | R | 1 | APPL.CtrlAppl.sParam.heatpump[1].HeatMeter.values.power | Actual power consumtion [kW]
732 | R | 1 | APPL.CtrlAppl.sParam.heatpump[1].ElectricEnergyMeter.values.power | Actual power consumtion [W]
733 | R | 10 | APPL.CtrlAppl.sParam.heatpump[1].TempSourceIn.values.actValue | Actual Source In temperature [1/10°C]
734 | R | 10 | APPL.CtrlAppl.sParam.heatpump[1].TempSourceOut.values.actValue | Actual Source Out temperature [1/10°C]
735 | R | 10 | APPL.CtrlAppl.sParam.heatpump[1].TempHeatReflux.values.actValue | Actual reflux temperature [1/10°C]
736 | R | 100 | APPL.CtrlAppl.sParam.heatpump[1].Source.values.setValueScaled | Source side actuator [1/10°C]
737 | R | 100 | APPL.CtrlAppl.sParam.heatpump[1].CircPump.values.setValueScaled | Heat side actuator
738 | R/W | 1 | APPL.CtrlAppl.sParam.heatpump[1].param.operatingMode | Heat pump operating mode. Selection from "0…Aus" / "1…Ein" / "2…Backup" | 0 | 2
739 | R | 1 | APPL.CtrlAppl.sDiagnosisData.heatpump[1].excessEnergy
740 | R | 0.001 | APPL.CtrlAppl.sStatisticalData.heatpump[1].consumption.energy | Total accumulated heating energy [MWh]
741 | R | 0.001 | APPL.CtrlAppl.sStatisticalData.heatpump[1].consumption.electricalenergy | Total accumulated electrical energy [MWh]
742 | R | 1 | APPL.CtrlAppl.sParam.heatpump[1].values.consumingExcessEnergy | Consuming Excess Energy
743 | R | 100 | APPL.CtrlAppl.sParam.heatpump[1].Compressor.analogOut.values.setValueScaled | Set value compressor
744 | R | 10 | APPL.CtrlAppl.sParam.heatpump[1].values.setTemp | Set temperature heat pump
745
746
747
748
749
heatpump[2]
750 | R | 0.00027778 | APPL.CtrlAppl.sStatisticalData.heatpump[2].consumption.operatingtime | Operating hours [h].
751 | R | 1 | APPL.CtrlAppl.sStatisticalData.heatpump[2].consumption.energy | Total accumulated heating energy [kWh]
752 | R | 1 | APPL.CtrlAppl.sStatisticalData.heatpump[2].consumption.electricalenergy | Total accumulated electrical energy [kWh]
753 | R | 1 | APPL.CtrlAppl.sParam.heatpump[2].values.heatpumpState | State heatpump. 0...Stanby, 1...PreRun, 2...AutomaticHeat, 3...Defrost, 4...AutomaticCool, 5...PostRun, 7...SafetyShutdown, 8...Error
754 | R | 1 | APPL.CtrlAppl.sParam.heatpump[2].TempHeatFlow.state.msgId | Message ID of the flow temperature sensor.
755 | R | 10 | APPL.CtrlAppl.sParam.heatpump[2].TempHeatFlow.values.actValue | Actual flow temperature [1/10°C].
756 | R | 1 | APPL.CtrlAppl.sParam.heatpump[2].HeatMeter.values.power | Actual power consumtion [kW]
757 | R | 1 | APPL.CtrlAppl.sParam.heatpump[2].ElectricEnergyMeter.values.power | Actual power consumtion [W]
758 | R | 10 | APPL.CtrlAppl.sParam.heatpump[2].TempSourceIn.values.actValue | Actual Source In temperature [1/10°C]
759 | R | 10 | APPL.CtrlAppl.sParam.heatpump[2].TempSourceOut.values.actValue | Actual Source Out temperature [1/10°C]
760 | R | 10 | APPL.CtrlAppl.sParam.heatpump[2].TempHeatReflux.values.actValue | Actual reflux temperature [1/10°C]
761 | R | 100 | APPL.CtrlAppl.sParam.heatpump[2].Source.values.setValueScaled | Source side actuator [1/10°C]
762 | R | 100 | APPL.CtrlAppl.sParam.heatpump[2].CircPump.values.setValueScaled | Heat side actuator
763 | R/W | 1 | APPL.CtrlAppl.sParam.heatpump[2].param.operatingMode | Heat pump operating mode. Selection from "0…Aus" / "1…Ein" / "2…Backup" | 0 | 2
764 | R | 1 | APPL.CtrlAppl.sDiagnosisData.heatpump[2].excessEnergy
765 | R | 0.001 | APPL.CtrlAppl.sStatisticalData.heatpump[2].consumption.energy | Total accumulated heating energy [MWh]
766 | R | 0.001 | APPL.CtrlAppl.sStatisticalData.heatpump[2].consumption.electricalenergy | Total accumulated electrical energy [MWh]
767 | R | 1 | APPL.CtrlAppl.sParam.heatpump[2].values.consumingExcessEnergy | Consuming Excess Energy
768 | R | 100 | APPL.CtrlAppl.sParam.heatpump[2].Compressor.analogOut.values.setValueScaled | Set value compressor
769 | R | 10 | APPL.CtrlAppl.sParam.heatpump[2].values.setTemp | Set temperature heat pump
770
771
772
773
774
heatpump[3]
775 | R | 0.00027778 | APPL.CtrlAppl.sStatisticalData.heatpump[3].consumption.operatingtime | Operating hours [h].
776 | R | 1 | APPL.CtrlAppl.sStatisticalData.heatpump[3].consumption.energy | Total accumulated heating energy [kWh]
777 | R | 1 | APPL.CtrlAppl.sStatisticalData.heatpump[3].consumption.electricalenergy | Total accumulated electrical energy [kWh]
778 | R | 1 | APPL.CtrlAppl.sParam.heatpump[3].values.heatpumpState | State heatpump. 0...Stanby, 1...PreRun, 2...AutomaticHeat, 3...Defrost, 4...AutomaticCool, 5...PostRun, 7...SafetyShutdown, 8...Error
779 | R | 1 | APPL.CtrlAppl.sParam.heatpump[3].TempHeatFlow.state.msgId | Message ID of the flow temperature sensor.
780 | R | 10 | APPL.CtrlAppl.sParam.heatpump[3].TempHeatFlow.values.actValue | Actual flow temperature [1/10°C].
781 | R | 1 | APPL.CtrlAppl.sParam.heatpump[3].HeatMeter.values.power | Actual power consumtion [kW]
782 | R | 1 | APPL.CtrlAppl.sParam.heatpump[3].ElectricEnergyMeter.values.power | Actual power consumtion [W]
783 | R | 10 | APPL.CtrlAppl.sParam.heatpump[3].TempSourceIn.values.actValue | Actual Source In temperature [1/10°C]
784 | R | 10 | APPL.CtrlAppl.sParam.heatpump[3].TempSourceOut.values.actValue | Actual Source Out temperature [1/10°C]
785 | R | 10 | APPL.CtrlAppl.sParam.heatpump[3].TempHeatReflux.values.actValue | Actual reflux temperature [1/10°C]
786 | R | 100 | APPL.CtrlAppl.sParam.heatpump[3].Source.values.setValueScaled | Source side actuator [1/10°C]
787 | R | 100 | APPL.CtrlAppl.sParam.heatpump[3].CircPump.values.setValueScaled | Heat side actuator
788 | R/W | 1 | APPL.CtrlAppl.sParam.heatpump[3].param.operatingMode | Heat pump operating mode. Selection from "0…Aus" / "1…Ein" / "2…Backup" | 0 | 2
789 | R | 1 | APPL.CtrlAppl.sDiagnosisData.heatpump[3].excessEnergy
790 | R | 0.001 | APPL.CtrlAppl.sStatisticalData.heatpump[3].consumption.energy | Total accumulated heating energy [MWh]
791 | R | 0.001 | APPL.CtrlAppl.sStatisticalData.heatpump[3].consumption.electricalenergy | Total accumulated electrical energy [MWh]
792 | R | 1 | APPL.CtrlAppl.sParam.heatpump[3].values.consumingExcessEnergy | Consuming Excess Energy
793 | R | 100 | APPL.CtrlAppl.sParam.heatpump[3].Compressor.analogOut.values.setValueScaled | Set value compressor
794 | R | 10 | APPL.CtrlAppl.sParam.heatpump[3].values.setTemp | Set temperature heat pump
795
796
797
798
799
800
801
802
803
804
805
806
807
808
809
810
811
812
813
814
815
816
817
818
819
820
821
822
823
824
825
826
827
828
829
830
831
832
833
834
835
836
837
838
839
840
841
842
843
844
845
846
847
848
849
850
851
852
853
854
855
856
857
858
859
860
861
862
863
864
865
866
867
868
869
870
871
872
873
874
875
876
877
878
879
880
881
882
883
884
885
886
887
888
889
890
891
892
893
894
895
896
897
898
899
997
998
999
photovoltaics
1000 | R/W | 1 | APPL.CtrlAppl.sIOModule.Virt[0].param.sensor[0] | Acutal excess energy given from Smart home System [W] | 0 | 20000
1001 | R | 1 | APPL.CtrlAppl.sIOModule.Virt[0].param.sensorErr[0] | Error of virtual excess energy
1002 | R | 1 | APPL.CtrlAppl.sParam.photovoltaics.ElectricEnergyMeter.values.power | Acutal excess energy given from Electricity Meter [W]
1003
1004
1005 | R/W | 1 | APPL.CtrlAppl.sParam.smartgrid.values.smartGridReadyOpMode | SG Ready operating mode (1…Betriebszustand 1 / 2…Betriebszustand 2 / 3… Betriebszustand 3 / 4… Betriebszustand 4) | 1 | 4
1006
1007
1008
1009
1010
1011
1012
1013
1014
1015
1016
1017
1018
1019
1020
1021
1022
1023
1024
1025
1026
1027
1028
1029
1030
1031
1032
1033
1034
1035
1036
1037
1038
1039
1040
1041
1042
1043
1044
1045
1046
1047
1048
1049
thermal solar
1050
1051
1052
1053
1054
1055
1056
1057
1058
1059
1060
1061
1062
1063
1064
1065
1066
1067
1068
1069
1070
1071
1072
1073
1074
1075
1076
1077
1078
1079
1080
1081
1082
1083
1084
1085
1086
1087
1088
1089
1090
1091
1092
1093
1094
1095
1096
1097
1098
1099
external request
1100 | R/W | 1 | APPL.CtrlAppl.sParam.externalRequest[0].param.digRequest | Boolean flag for external request. Same functionality as digital input in hardware. | 0 | 1
1101 | R/W | 10 | APPL.CtrlAppl.sParam.externalRequest[0].param.digRequestTemp | Request temperature (°C) when DI or boolean flag is set. | 20 | 120
1102
1103
1104
1105
1106
1107
1108
1109
1110
1111
1112
1113
1114
1115
1116
1117
1118
1119
1120
1121
1122
1123
1124
system alarms
1450 | R | 1 | APPL.CtrlAppl.sParam.values.pendingAlarms.ID0 | ID of 1st pending alarm. 0 if no alarm.
1451 | R | 1 | APPL.CtrlAppl.sParam.values.pendingAlarms.ID1 | ID of 2nd pending alarm. 0 if no alarm.
1452 | R | 1 | APPL.CtrlAppl.sParam.values.pendingAlarms.ID2 | ID of 3rd pending alarm. 0 if no alarm.
1453 | R | 1 | APPL.CtrlAppl.sParam.values.pendingAlarms.ID3 | ID of 4th pending alarm. 0 if no alarm.
1454 | R | 1 | APPL.CtrlAppl.sParam.values.pendingAlarms.ID4 | ID of 5th pending alarm. 0 if no alarm.
1455 | R | 1 | APPL.CtrlAppl.sParam.values.pendingAlarms.ID5 | ID of 6th pending alarm. 0 if no alarm.
1456 | R | 1 | APPL.CtrlAppl.sParam.values.pendingAlarms.ID6 | ID of 7th pending alarm. 0 if no alarm.
1457 | R | 1 | APPL.CtrlAppl.sParam.values.pendingAlarms.ID7 | ID of 8th pending alarm. 0 if no alarm.
1458 | R | 1 | APPL.CtrlAppl.sParam.values.pendingAlarms.ID8 | ID of 9th pending alarm. 0 if no alarm.
1459 | R | 1 | APPL.CtrlAppl.sParam.values.pendingAlarms.ID9 | ID of 10th pending alarm. 0 if no alarm.
1460
1461
1462
1463
1464
1465
1466
1467
1468
1469
1470 | R/W | 1 | APPL.CtrlAppl.sParam.external.quitAllAlarms | Reset Alarms by Modbus | 0 | 1
1471
1472
1473
1474
system
1500 | R/W | 1 | APPL.CtrlAppl.sParam.param.operatingMode | Operating Mode of the system: Setup (-1), Standby (0), Summer (1), AutoHeat (2), AutoCool (3), FullAuto (4) | -1 | 4
1501 | R | 1 | APPL.CtrlAppl.sParam.outdoorTemp.state.msgId | Message ID of the outdoor temperature sensor.
1502 | R | 10 | APPL.CtrlAppl.sParam.outdoorTemp.values.actValue | Actual exterior temperature [°C].
1503 | R/W | 10 | APPL.CtrlAppl.sIOModule.Virt[0].param.sensor[1] | Acutal exterior temperature [°C] given from Smart home System [W] | -100 | 100
1504 | R | 1 | APPL.CtrlAppl.sIOModule.Virt[0].param.sensorErr[1] | Error of virtual exterior temperature
1505
1506
1507
1508
1509
1510
1511
1512
1513
1514
1515
1516
1517 | R | 1 | APPL.CtrlAppl.sStatisticalData.heatpump[0].consumption.energy | Total accumulated heating energy [kWh]
1518 | R | 1 | APPL.CtrlAppl.sStatisticalData.heatpump[0].consumption.energy | Total accumulated heating energy [kWh]
1519 | R | 1 | APPL.CtrlAppl.sStatisticalData.heatpump[1].consumption.energy | Total accumulated heating energy [kWh]
1520 | R | 1 | APPL.CtrlAppl.sStatisticalData.heatpump[1].consumption.energy | Total accumulated heating energy [kWh]
1521 | R | 1 | APPL.CtrlAppl.sStatisticalData.heatpump[2].consumption.energy | Total accumulated heating energy [kWh]
1522 | R | 1 | APPL.CtrlAppl.sStatisticalData.heatpump[2].consumption.energy | Total accumulated heating energy [kWh]
1523 | R | 1 | APPL.CtrlAppl.sStatisticalData.heatpump[3].consumption.energy | Total accumulated heating energy [kWh]
1524 | R | 1 | APPL.CtrlAppl.sStatisticalData.heatpump[3].consumption.energy | Total accumulated heating energy [kWh]
external heatsource
1600 | R/W | 100 | APPL.CtrlAppl.sParam.extHeatSource[0].param.externalSetvalueScaled | Control of the heat source by an external control [100%] | 0 | 100
1601 | R | 1 | APPL.CtrlAppl.sParam.extHeatSource[0].values.requestExtHeatsource | 0…no request, external heat source must be turned off. 1…external heat source is released and can be switched on. 2…external heat source is required and must be turned on.
1602 | R | 1 | APPL.CtrlAppl.sParam.extHeatSource[0].values.consumingExcessEnergy | Use Excess Energy
1603 | R | 1 | APPL.CtrlAppl.sParam.extHeatSource[0].DO.values.setValueB | request External Heat Source

## Modbus Interface Doku
Modbus Interface Dokumentation
1. Allgemeines
1.1. Beschreibung
Das M-TEC Steuerungssystem mit Modbus-Server unterstützt das Schreiben und Lesen von Variablen über die Modbus-Schnittstelle.
Die zur Verfügung gestellten Variablen sind in diesem Excel File unter dem Reiter „Modbusvariablen“ zu finden.
1.2. Interface
Es wird folgende Schnittstelle verwendet:
· Ethernet, Port 502, Slave Adress 1
1.3. Folgendes Protokoll wird unterstützt:
· Modbus TCP
Funktionen
Funktions-Code |  | Name
0x01 |  | Read Register (Funktion wird nicht Verwendet)
0x03 |  | Read Holding Registers
0x06 |  | Write Single Register
0x10 |  | Write Multiple Registers
Diese Funktionscodes werden vom Modbus-Server unterstützt.
2. Modbus Server Details
Der Modbus-Server wird gestartet, wenn der erste Socket geöffnet wird. Daher kann die erste Antwort bis zu 10s verzögert sein.
Andere Funktionscodes werden mit der Fehlerantwort: MODBUS_EXCEPTION_ILLEGAL_FUNCTION verworfen.
Wird ein Register aufgerufen, welches nicht in der Variablenbelegung parametriert ist oder ein Schreibversuch ohne Schreibberechtigung darauf unternommen wird, wird die
Fehlerantwort MODBUS_EXCEPTION_ILLEGAL_DATA_ADDRESS gesendet.
2.1 Fehler Codes
Die folgenden Fehlercodes werden an den Modbus-Client gesendet.
Fehlercode |  |  | Nr. | Beschreibung
MODBUS_EXCEPTION_ILLEGAL_FUNCTION |  |  | 1 | Modbus-Funktion wird nicht unterstützt
MODBUS_EXCEPTION_ILLEGAL_DATA_ADDRESS |  |  | 2 | - Die Registeradresse existiert nicht
- Mehrfachzugriff (schreiben oder lesen) über die Grenzen der Registeradressen
- Keine Schreibberechtigung für die Registeradresse
- Kein gültiger Zugriff auf verbundene Register (z. B .: nur ein Register eines verbundenen Variable wird gelesen)
MODBUS_EXCEPTION_ILLEGAL_DATA_VALUE |  |  | 3 | -Maximale Anzahl für Register per Befehl
“write_multiple_registers” überschritten
MODBUS_EXCEPTION_SLAVE_OR_SERVER_FAILURE |  |  | 4 | - Modbus Server hat ungültige Register- Konfigurationsdatei gelesen
- Steuerung läuft nicht
2.2. Register Parametrierung
Es werden folgenden Parameter für die Konfiguration des Modbus-Servers verwendet:
· Modbus-Registerbelegung
· Schreibzugriff
· Interner Variablenname
· Umrechnungsfaktor
Beispiel:
Modbus Register | Zugriff | Faktor | Variablen Name |  | Beschreibung
0 | R | 0 | APPL.CtrlAppl.sParam.heatpump[0].Te mpHeatFlow.values.actValue
1 | R | 0 | APPL.CtrlAppl.sParam.heatpump[0].Te mpHeatFlow.values.actValue
2 | R | 1 | APPL.CtrlAppl.sParam.heatpump[0].Te mpHeatFlow.state.msgId
3 | R/W | 100 | APPL.CtrlAppl.sParam.heatCircuit[0].param.normalSetTemp
….
Die Modbuserver-Register beginnen mit Index 0. Kunden-Implementierungen müssen dahingehend abgestimmt sein.
Modbus unterstützt nur 16-Bit-Register. Diese Register können nur ganzzahlige Werte
ohne Nachkommastellen darstellen.
Daher benötigen Werte welche mit Gleitkomma dargestellt werden einen Umrechnungsfaktor. Vorzeichenlose ganzzahlige Werte größer als 65536 bzw. vorzeichenbehaftete Ganzzahlwerte größer/kleiner als +/- 32768 werden über 2 Modbus-Register übertragen.
Übertragung eines 32-Bit-Float-Wertes über Umrechnungsfaktor und Single-Register Zugriff
Die Variable
APPL.CtrlAppl.sParam.heatCircuit [0] .param.normalSetTemp
von der Beispielparametertabelle ist als Einzelregister mit dem Umrechnungsfaktor 100 parametriert.
Wenn Sie diese Variable lesen, wird der Wert vor dem Senden über Modbus mit dem Umrechnungsfaktor multipliziert.
Auf der Client-Seite empfangene Daten müssen durch Teilen mit dem Faktor, zurückkonvertiert werden um den Wert zu erhalten.
Beispiel:
Die Solltemperatur des Heizkreis 1 beträgt:
APPL.CtrlAppl.sParam.heatCircuit [0] .param.normalSetTemp = 23,456 ° C
Der Wert wird mit dem Umrechnungsfaktor 100 multipliziert und in einen ganzzahligen Wert umgewandelt.
23,456 * 100 = 2345,6 è Ganzzahlumwandlung (ohne Rundung) è 2345
Der Wert 2345 wird über Modbus übertragen.